## Sheet1
Given conditions
Location: |  | Sheopur
Type of building: |  |  |  | School
Number of floors: |  |  |  | 2
Wall area: |  |  |  | First Exposed Wall: | 150.5 ft^2 | Second Exposed Wall |  | 178.5 ft^2
No of Room per floor: |  |  |  | 14
Area of roof |  |  |  | 300.625 | ft^2 | (18.5*16.25)ft^2
Floor -to-floor height: |  |  |  |  | 11ft
Window area: |  |  |  | 25 ft^2
Windows: |  | Single glazed
Door |  | Single |  | Area : 28 ft^2
Number of Windows: |  |  |  | 2
Overall Heat Transfer Coefficient (U) |  |  |  |  | in | BTU/h.ft^2.F
Exposed wall |  | 0.282 |  | Brick wall
Partition wall |  | 0.282 |  | Brick wall
Ground Floor |  | 0.291 |  | light weight concrete
First floor |  | 0.264 |  | 6" light weight concrete
Ceiling(2nd Floor) .7 |  | 0.277 |  | 6" light weight concrete
Window |  | 0.51 |  | Double glazed of 6mm
Recommended Ventilation |  |  |  |  | 20 | cfm/person
Occupancy of room |  |  |  | 5 person per 300.625 ft^2
Working hours: |  |  |  | 6 hrs
Design conditions
Location: |  | (25°40'N 76°41'E) |  |  | For simplicity considering 26.4° N | 24degreeN
Outdoor design dry-bulb: |  |  |  |  | 109.4 | °F
Outdoor design Wet-bulb: |  |  |  |  | 86 | °F
Indoor design dry-bulb: |  |  |  |  | 77 | °F
Daily range: |  |  |  |  | 19.8 | °F
Relative humidity: |  |  |  |  | 40%
Wind velocity: |  |  |  |  | 6.2 | mph
CLTD |  | (cooling load temp difference) |  |  |  | 32.4 |  | (Outdoor temperature - Indoor temperature)
calculation of CLTD Correction |  |  |  |  | = | [CLTD+(78-INSIDE DESIGN TEMP)+(Mean outdoor temperature-85)]
Mean outdoor tempearature |  |  |  |  | = | (outdoor design dry bulb temperature-(daily range/2))
CLTD (correction) |  |  |  | 15.5
Mean outdoor tempearature |  |  |  |  | 99.5
[5 empty] | External Wall | Heat load calculation
Facing Direction |  | Total | No of Wall | Inside design | outdoor | Daily range |  | Mean outdoor |  |  | CLTD | CLTDc | U | Wall
|  | Area |  | temperature | temperature |  |  | temperature
1st and 2nd floor |  |  |  | °F | °F | °F |  | °F |  |  | °F | °F |  | Sensible Load
East |  | 178.75 | 2 | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 18 | 33.5 | 0.282 | 3377.3025
East |  | 150.5 | 14 | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 18 | 33.5 | 0.282 | 19904.829
[13 empty] | Total | 23282.1315
Facing Direction |  | Total |  | Inside design | outdoor | Daily range |  | Mean outdoor |  |  | CLTD | CLTDc | U | Sensible Load
|  | AREA (ft^2 |  | temperature | temperature |  |  | temperature
1st and 2nd floor |  |  |  | °F | °F | °F |  | °F |  |  | °F | °F
West |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 22 | 37.5 | 0.282 | 3775.275
West |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 22 | 37.5 | 0.282 | 3775.275
West |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 22 | 37.5 | 0.282 | 3775.275
West |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 22 | 37.5 | 0.282 | 3775.275
West |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 22 | 37.5 | 0.282 | 3775.275
West |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 22 | 37.5 | 0.282 | 3775.275
West |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 22 | 37.5 | 0.282 | 3775.275
West |  | 307.5 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 22 | 37.5 | 0.282 | 3251.8125
[13 empty] | Total | 29678.7375
Facing Direction |  | Total |  | Inside design | outdoor | Daily range |  | Mean outdoor |  |  | CLTD | CLTDc | U | Sensible Load
|  | AREA (ft^2) |  | temperature | temperature |  |  | temperature
1st and 2nd floor |  |  |  | °F | °F | °F |  | °F |  |  | °F | °F
North |  | 301 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 6 | 21.5 | 0.282 | 1824.963
North |  | 301 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 6 | 21.5 | 0.282 | 1824.963
North |  | 301 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 6 | 21.5 | 0.282 | 1824.963
North |  | 301 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 6 | 21.5 | 0.282 | 1824.963
North |  | 301 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 6 | 21.5 | 0.282 | 1824.963
North |  | 301 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 6 | 21.5 | 0.282 | 1824.963
North |  | 357.5 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 6 | 21.5 | 0.282 | 2167.5225
[13 empty] | Total | 13117.3005
Facing Direction |  | Total |  | Inside design | outdoor | Daily range |  | Mean outdoor |  |  | CLTD | CLTDc | U | Sensible Load
|  | AREA (ft^2 |  | temperature | temperature |  |  | temperature
1st and 2nd floor |  |  |  | °F | °F | °F |  | °F |  |  | °F | °F
South |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 11 | 26.5 | 0.282 | 2667.861
South |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 11 | 26.5 | 0.282 | 2667.861
South |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 11 | 26.5 | 0.282 | 2667.861
South |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 11 | 26.5 | 0.282 | 2667.861
South |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 11 | 26.5 | 0.282 | 2667.861
South |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 11 | 26.5 | 0.282 | 2667.861
South |  | 357 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 11 | 26.5 | 0.282 | 2667.861
[13 empty] | TOTaL | 18675.027
Partition wall heat load
|  | Type | Area | CLTD | CLTDc | U | No of wall | Sensible Load
|  | Shaded | 178.75 | 4 | 19.5 | 0.282 | 4 | 3931.785
|  |  | Area | No. of wall | Temp diff(delT) | U |  | Sensible Load
|  | Between adjacent room | 178.75 | 11 | 0 | 0.282 |  | 0
Door Heat Load Calculation
Direction |  | Area of door | no of door | CLTD | CLTDc | U | Sensible heat Load
East |  | 28 | 14 | 18 | 33.5 | 0.44 | 5778.08
North |  | 28 | 14 | 6 | 21.5 | 0.44 | 3708.32
[6 empty] | Total | 9486.4
Ground Floor heat Load
Room No. |  | Total |  | Inside design | outdoor | Daily range |  | Mean outdoor |  |  | CLTD | CLTDc | U | Sensible
|  | AREA (ft^2) |  | temperature | temperature |  |  | temperature | [5 empty] | Load
Ground floor |  |  |  | °F | °F | °F |  | °F |  |  | °F | °F
All direction |  | 4208.75 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 4 | 19.5 | 0.291 | 23882.5519
Roof Heat Load Calculation
Room No. |  | Total |  | Inside design | outdoor | Daily range |  | Mean outdoor |  |  | CLTD | CLTDc | U | Sensible
|  | AREA (ft^2) |  | temperature | temperature |  |  | temperature | [5 empty] | Load
Top floor |  |  |  | °F | °F | °F |  | °F |  |  | °F | °F
All direction |  | 4208.75 |  | 77 | 109.4 | 19.8 |  | 99.5 |  |  | 43 | 58.5 | 0.277 | 68200.6894
Windows Heat Load Calculation (Double glass glazed)
Conduction
Room No. |  | CLTD |  | CLTDc | U | Total Area |  | Heat Load
Calculation
1st and 2nd Floor
East |  | 10 |  | 25.5 | 0.51 | 350 |  | 4551.75
West |  | 10 |  | 25.5 | 0.51 | 400 |  | 5202
North |  | 10 |  | 25.5 | 0.51 | 300 |  | 3901.5
South |  | 10 |  | 25.5 | 0.51 | 350 |  | 4551.75
[6 empty] | Total Load |  | 18207
Radiation
Room No. |  | Total |  | Shading Coeffcient | CLF | SHGF | Solar cooling load | Heat Load
|  | Area |  | SC |  |  | Factor (SCL) | Calculation
1st and 2nd Floor
East |  | 350 |  | 0.25 | 0.47 | 167 | 78.49 | 6867.875
West |  | 400 |  | 0.25 | 0.53 | 118 | 62.54 | 6254
North |  | 300 |  | 0.25 | 0.24 | 41 | 9.84 | 738
South |  | 350 |  | 0.25 | 0.5 | 41 | 20.5 | 1793.75
[7 empty] | Total | 15653.625
Occupancy Load Calculation
No of room |  | No of person |  | Sesnible Load |  | Latent Load Per | Total sensible Load | Total Latent |  |  |  | Total Occupancy Load
|  | per room |  | Per Person |  | Person |  | Load
28 |  | 5 |  | 250 |  | 200 | 35000 | 28000 |  |  |  | 63000
Infilteration Load Calculation
No. of |  | cfm per | No. of Persons | CFM | outdoor | Indoor | Sensible Heat |  |  |  | Specific humidity | Specific humidy | Latent |  |  | Total Infilteration Load
Room |  | person | per room |  | temperature | temperature | Gain |  |  |  | at 109.4 F & 40% RH | at 77 F, 55% RH | Load
28 |  | 20 | 5 | 2800 | 109.4 | 77 | 97977.6 |  |  |  | 0.022 | 0.011 | 149072 |  |  | 247049.6
Ventilation Load Calculation
No. of |  | cfm per | No. of Persons | CFM | outdoor | coil | Sensible Heat |  |  |  | Specific humidity | Specific humidy | Latent |  | Total Ventilation Load
Room |  | person | per room |  | temperature | temperature | Gain |  |  |  | at 109.4 F & 40% RH | at 50 F, ADP | Load
28 |  | 20 | 5 | 2800 | 109.4 | 50 | 179625.6 |  |  |  | 0.022 | 0.0076 | 195148.8 |  |  | 374774.4
Lightning Load
[5 empty] | Total Load in | Total Load
Location |  |  | Rule of Thumb | Total area | watt | in BTU/hr
watt per sq ft
school |  |  | 1 | 4208.75 | 4208.75 | 14360.8511
Appliances Load
[11 empty] | Total lightning load |  | Appliances Load |  |  | Total Appliances Load
Equipment |  | no. of | Name Plate | Name Plate Power | Heat Load | Heat Load in |  |  |  |  | 14360.8511 |  | 13757.184 |  |  |  | 28118.0351
|  | Equipment | Power Rating | Consumption | in watt | BTU/Hr
Desktop |  | 28 | 480 | 13440 | 4032 | 13757.184
Computer
Total Wall Load
|  | East | West | North | South |  | Total
External wallLoad |  | 23282.1315 | 29678.7375 | 13117.3005 | 18675.027 |  | 84753.1965
Ground Floor Load | [6 empty] | 23882.5519
Door heat Load |  | 5778.08 |  | 3708.32 |  |  | 9486.4
Partition wall heat Load | [6 empty] | 3931.785
[6 empty] | Total Wall Load | 122053.9334
Total window Heat Load
By Conduction |  |  | By Radiation |  |  | Total Window Load
18207 |  |  | 15653.625 |  |  | 33860.625
Total Load Analysis
Total wall Load | Total Roof Load | Total Window Load | Total Load by window ,wall roof
122053.9334 | 68200.6894 | 33860.625 | 224115.2477
Total Load by window ,wall and Roof |  |  | 224115.2477 | 23.92%
Ventilation Total Load |  |  | 374774.4 | 39.99%
Infiltration Total Load |  |  | 247049.6 | 26.36%
Appliances Load |  |  | 28118.0351 | 3.001%
Occupancy Total Load |  |  | 63000 | 6.723%
|  | Total | 937057.2828
Serial No. |  | Type | Sensible Heat | Latent Heat |  | Total Heat Load
1 |  | Wall Load | 122053.9334 |  |  | 122053.9334
2 |  | Roof Load | 68200.6894 |  |  | 68200.6894
3 |  | Window Load | 33860.625 |  |  | 33860.625
4 |  | Ventilation | 179625.6 | 195148.8 |  | 374774.4
5 |  | Infilteration | 97977.6 | 149072 |  | 247049.6
6 |  | Appliances | 28118.0351 |  |  | 28118.0351
7 |  | Occupancy | 35000 | 28000 |  | 63000
|  | TOTAL | 564836.4828 | 372220.8 | 0 | 937057.2828 | 78.0881 | TR
Single Room Total Load Analysis In 1 Ton of Refrigeration
Single Room with two wall exposed to Sun
Direction | Room | East face wall load | West face load | Roof Load | Windows Load | Ventilation load | infilteration load | occupancy | Ground floor load | Door Load Calculation | appliances | Grand Total | Grand Total
[12 empty] | in BTU/Hr | in TR
Ground Floor East facing | GE2,GE3,GE4,GE5,GE6 | 1421.7735 | 1887.6375 | 0 | 1633.9732 | 13384.8 | 8823.2 | 2250 | 852.9483 | 412.72 | 1004.2155 | 31671.268 | 2.6393
[12 empty] | 0 | 0
First Floor East facing | FE2, FE3, FE4,FE5, FE6, , | 1421.7735 | 1887.6375 | 2435.7389 | 1633.9732 | 13384.8 | 8823.2 | 2250 | 0 | 412.72 | 1004.2155 | 33254.0587 | 2.7712
[12 empty] | 0 | 0
|  | North face wall Load | South face wall load | [8 empty] | 0 | 0
Ground Floor North Facing | GN2,GN3,GN4, GN5,GN6 | 912.4815 | 1333.9305 | 0 | 784.6429 | 13384.8 | 8823.2 | 2250 | 852.9483 | 264.88 | 1004.2155 | 29611.0987 | 2.4676
[12 empty] | 0 | 0
[12 empty] | 0 | 0
First Floor | FN2,FN3,FN4 | 912.4815 | 1333.9305 | 2435.7389 | 784.6429 | 13384.8 | 8823.2 | 2250 | 0 | 264.88 | 1004.2155 | 31193.8893 | 2.5995
North Facing | FN5,FN6
Single Room with Three wall exposed to Sun
Direction | Room | East Face wall Load | West face wall Load | north face wall load | south facing wall Load | Roof Load | Windows Load | Ventilation Load | Infiltration Load | Occupancy Load | Door Load | Ground Loor Load | Appliances | Grand Total in Btu/h | Grand Total on TR
Ground Floor East facing | GE7 | 1421.7735 | 1887.6375 | 1083.7612 | 0 | 0 | 1633.9732 | 13384.8 | 8823.2 | 2250 | 412.72 | 852.9483 | 1004.2155 | 32755.0293 | 2.7296
First Floor East Facing | FE7 | 1421.7735 | 1887.6375 | 1083.7612 | 0 | 2435.7389 | 1633.9732 | 13384.8 | 8823.2 | 2250 | 412.72 | 0 | 1004.2155 | 34337.8199 | 2.8615
Ground Floor North facing | GN7 | 1688.6512 | 0 | 912.4815 | 1333.9305 | 0 | 784.6429 | 13384.8 | 8823.2 | 2250 | 264.88 | 852.9483 | 1004.2155 | 31299.7499 | 2.6083
First Floor North Facing | FN7 | 1688.6512 | 0 | 912.4815 | 1333.9305 | 2435.7389 | 784.6429 | 13384.8 | 8823.2 | 2250 | 264.88 | 0 | 1004.2155 | 32882.5406 | 2.7402
Single Room with two wall exposed and one shaded wall
Direction | Room | East Face wall Load | West face wall Load | north/South face wall load | shaded wall Load | Roof Load | Windows Load | Ventilation Load | Infiltration Load | Occupancy Load | Door Load | Ground Loor Load | Appliances | Grand Total in Btu/h | Grand Total on TR
Ground Floor East facing | GE1 | 1421.7735 | 1887.6375 | 0 | 982.9462 | 0 | 1633.9732 | 13384.8 | 8823.2 | 2250 | 412.72 | 852.9483 | 1004.2155 | 32654.2143 | 2.7212
First Floor East Facing | FE1 | 1421.7735 | 1887.6375 | 0 | 982.9462 | 2435.7389 | 1633.9732 | 13384.8 | 8823.2 | 2250 | 412.72 | 0 | 1004.2155 | 34237.0049 | 2.8531
Ground Floor North facing | GN1 | 0 | 1625.9062 | 912.4815 | 982.9462 | 0 | 1169.25 | 13384.8 | 8823.2 | 2250 | 264.88 | 852.9483 | 1004.2155 | 31270.6278 | 2.6059
First Floor North Facing | FN1 | 0 | 1625.9062 | 912.4815 | 982.9462 | 2435.7389 | 1169.25 | 13384.8 | 8823.2 | 2250 | 264.88 | 0 | 1004.2155 | 32853.4184 | 2.7378